## Sheet1
Icemaking
Partial Storage
Hour Ending | Chiller Plant Mode | Building load (tons) | 1st Chiller Use (tons) | 1st Ice Dispatch | 2nd Chiller Usage | 2nd Ice Dispatch | Revised Chiller Use | Revised Ice Dispatch | Full Storage
1 | Icemaking | 0 | 367.25 | 0 |  |  | 367.25 | 0
2 | Icemaking | 0 | 367.25 | 0 |  |  | 367.25 | 0
3 | Icemaking | 0 | 367.25 | 0 |  |  | 367.25 | 0
4 | Icemaking | 0 | 367.25 | 0 |  |  | 367.25 | 0
5 | Icemaking | 0 | 367.25 | 0 |  |  | 367.25 | 0
6 | Icemaking | 0 | 367.25 | 0 |  |  | 367.25 | 0
7 | Partial Storage | 200 | 200 | 0 |  |  | 200 | 0
8 | Partial Storage | 300 | 300 | 0 |  |  | 300 | 0
9 | Partial Storage | 400 | 400 | 0 |  |  | 400 | 0
10 | Partial Storage | 500 | 500 | 0 |  |  | 500 | 0
11 | Partial Storage | 800 | 565 | 235 |  |  | 544.9773 | 255.0227
12 | Partial Storage | 1000 | 565 | 435 |  |  | 544.9773 | 455.0227
13 | Partial Storage | 1000 | 565 | 435 |  |  | 544.9773 | 455.0227
14 | Partial Storage | 1000 | 565 | 435 |  |  | 544.9773 | 455.0227
15 | Partial Storage | 1000 | 565 | 435 |  |  | 544.9773 | 455.0227
16 | Partial Storage | 1000 | 565 | 435 |  |  | 544.9773 | 455.0227
17 | Partial Storage | 900 | 565 | 335 |  |  | 544.9773 | 355.0227
18 | Partial Storage | 800 | 565 | 235 |  |  | 544.9773 | 255.0227
19 | Partial Storage | 600 | 565 | 35 |  |  | 544.9773 | 55.0227
20 | Partial Storage | 600 | 565 | 35 |  |  | 544.9773 | 55.0227
21 | Partial Storage | 600 | 565 | 35 |  |  | 544.9773 | 55.0227
22 | Icemaking | 0 | 367.25 | 0 |  |  | 367.25 | 0
23 | Icemaking | 0 | 367.25 | 0 |  |  | 367.25 | 0
24 | Icemaking | 0 | 367.25 | 0 |  |  | 367.25 | 0
Sum |  | 10700 | 10920.25 | 3085 |  |  | 10700 | 3305.25
Max
Icemaking hrs: | 9
Partial Storage hrs: | 15
Full Storage hrs: | 0
Diversity factor: | 71.33%
Min Chiller Size: | 513.1894
Add 10%: | 565 | 10% "cushion" - margin for error/load growth
Storage ton-hrs: | 3002.1583
Tanks: | 21
Charge t-h: | 3305.25
Discharge1 t-h: | 3085
Max Original Output: | 565
Hrs at max: | 11
Tons that can be shaven: | 20.0227

## v2
Icemaking
[11 empty] | =IF(I4>=$C$46,$C$49,I4) |  |  |  | Partial Storage
Hour Ending | Chiller Plant Mode | Building load (tons) | 1st Chiller Use (tons) | 1st Ice Dispatch | 2nd Chiller Usage | 2nd Ice Dispatch | 3rd Chiller Use | 3rd Ice Dispatch | IsHighest, 3ID | MaxDis | 4th Chiller Use | 4th Ice Dispatch | 5th Chiller Use | 5th Ice Dispatch | Full Storage
1 | Icemaking | 0 | 333.5731 | 0 | 412.7596 | 0 | 412.7596 | 0 |  |  | 412.7596 | 0 | 412.7596 | 0 | Chiller Only
2 | Icemaking | 0 | 333.5731 | 0 | 412.7596 | 0 | 412.7596 | 0 |  |  | 412.7596 | 0 | 412.7596 | 0
3 | Icemaking | 0 | 333.5731 | 0 | 412.7596 | 0 | 412.7596 | 0 |  |  | 412.7596 | 0 | 412.7596 | 0
4 | Icemaking | 0 | 333.5731 | 0 | 412.7596 | 0 | 412.7596 | 0 |  |  | 412.7596 | 0 | 412.7596 | 0
5 | Icemaking | 0 | 333.5731 | 0 | 412.7596 | 0 | 412.7596 | 0 |  |  | 412.7596 | 0 | 412.7596 | 0
6 | Icemaking | 0 | 333.5731 | 0 | 412.7596 | 0 | 412.7596 | 0 |  |  | 412.7596 | 0 | 412.7596 | 0
7 | Partial Storage | 200 | 200 | 0 | 200 | 0 | 200 | 0 |  |  | 200 | 0 | 200 | 0
8 | Partial Storage | 300 | 300 | 0 | 300 | 0 | 300 | 0 |  |  | 300 | 0 | 300 | 0
9 | Partial Storage | 400 | 400 | 0 | 400 | 0 | 400 | 0 |  |  | 400 | 0 | 400 | 0
10 | Partial Storage | 500 | 500 | 0 | 500 | 0 | 500 | 0 |  |  | 507.0969 | -7.0969 | 507.0969 | -7.0969
11 | Partial Storage | 800 | 513.1894 | 286.8106 | 635.0148 | 164.9852 | 473.1454 | 326.8546 |  |  | 507.0969 | 292.9031 | 507.6883 | 292.3117
12 | Partial Storage | 1000 | 513.1894 | 486.8106 | 635.0148 | 364.9852 | 473.1454 | 526.8546 | x | 473.1454 | 507.0969 | 492.9031 | 507.6883 | 492.3117
13 | Partial Storage | 1000 | 513.1894 | 486.8106 | 635.0148 | 364.9852 | 473.1454 | 526.8546 | x | 473.1454 | 507.0969 | 492.9031 | 507.6883 | 492.3117
14 | Partial Storage | 1000 | 513.1894 | 486.8106 | 635.0148 | 364.9852 | 473.1454 | 526.8546 | x | 473.1454 | 507.0969 | 492.9031 | 507.6883 | 492.3117
15 | Partial Storage | 1000 | 513.1894 | 486.8106 | 635.0148 | 364.9852 | 473.1454 | 526.8546 | x | 473.1454 | 507.0969 | 492.9031 | 507.6883 | 492.3117
16 | Partial Storage | 1000 | 513.1894 | 486.8106 | 635.0148 | 364.9852 | 473.1454 | 526.8546 | x | 473.1454 | 507.0969 | 492.9031 | 507.6883 | 492.3117
17 | Partial Storage | 900 | 513.1894 | 386.8106 | 635.0148 | 264.9852 | 473.1454 | 426.8546 |  |  | 507.0969 | 392.9031 | 507.6883 | 392.3117
18 | Partial Storage | 800 | 513.1894 | 286.8106 | 635.0148 | 164.9852 | 473.1454 | 326.8546 |  |  | 507.0969 | 292.9031 | 507.6883 | 292.3117
19 | Partial Storage | 600 | 513.1894 | 86.8106 | 600 | 0 | 600 | 0 |  |  | 507.0969 | 92.9031 | 507.6883 | 92.3117
20 | Partial Storage | 600 | 513.1894 | 86.8106 | 600 | 0 | 600 | 0 |  |  | 507.0969 | 92.9031 | 507.6883 | 92.3117
21 | Partial Storage | 600 | 513.1894 | 86.8106 | 600 | 0 | 600 | 0 |  |  | 507.0969 | 92.9031 | 507.6883 | 92.3117
22 | Icemaking | 0 | 333.5731 | 0 | 412.7596 | 0 | 412.7596 | 0 |  |  | 412.7596 | 0 | 412.7596 | 0
23 | Icemaking | 0 | 333.5731 | 0 | 412.7596 | 0 | 412.7596 | 0 |  |  | 412.7596 | 0 | 412.7596 | 0
24 | Icemaking | 0 | 333.5731 | 0 | 412.7596 | 0 | 412.7596 | 0 |  |  | 412.7596 | 0 | 412.7596 | 0
Sum |  | 10700 | 10047.2422 | 3654.9161 | 11994.9555 | 2419.8813 | 10700 | 3714.8368 |  |  | 10700 | 3714.8368 | 10706.5055 | 3708.3313
Max |  | 1000 | 513.1894 | 486.8106 | 635.0148 | 364.9852 | 600 | 526.8546 | 526.8546 | 473.1454 | 507.0969 | 492.9031 | 507.6883 | 492.3117
[9 empty] | 5 |  | 12
Icemaking hrs: | 9
Partial Storage hrs: | 15
Full Storage hrs: | 0
Diversity factor: | 71.33%
Min Chiller Size: | 513.1894
2nd Partial Storage hrs: | 11
2nd Chiller size: | 635.0148
Storage ton-hrs: | 3714.8368
Tanks: | 26
Charge t-h: | 3714.8368
Discharge2 t-h: | 2419.8813
Max Original Output: | 635.0148
Hrs at max: | 8
Tons that can be shaven: | 161.8694
3rd run chiller opt: | 473.1454 | <---got to get the baseline
Hrs at or above chiller opt: | 12
available t-h: | 407.4184
avg. >= max: | 507.0969
false t-h: | 7.0969

## v3
Icemaking
[11 empty] | =IF(I4>=$C$46,$C$49,I4) |  |  |  | Partial Storage
Hour Ending | Chiller Plant Mode | Building load (tons) | 1st Chiller Use (tons) | 1st Ice Dispatch | 2nd Chiller Usage | 2nd Ice Dispatch | 3rd Chiller Use | 3rd Ice Dispatch | IsHighest, 3ID | MaxDis | 4th Chiller Use | 4th Ice Dispatch | 5th Chiller Use | 5th Ice Dispatch | Full Storage
1 | Icemaking | 0 | 624.2424 | 0 | 995.3202 | 0 | 995.3202 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0 | Chiller Only
2 | Icemaking | 0 | 624.2424 | 0 | 995.3202 | 0 | 995.3202 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
3 | Icemaking | 0 | 624.2424 | 0 | 995.3202 | 0 | 995.3202 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
4 | Icemaking | 0 | 624.2424 | 0 | 995.3202 | 0 | 995.3202 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
5 | Icemaking | 0 | 624.2424 | 0 | 995.3202 | 0 | 995.3202 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
6 | Icemaking | 0 | 624.2424 | 0 | 995.3202 | 0 | 995.3202 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
7 | Chiller Only | 200 | 200 | 0 | 200 | 0 | 200 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
8 | Chiller Only | 300 | 300 | 0 | 300 | 0 | 300 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
9 | Chiller Only | 400 | 400 | 0 | 400 | 0 | 400 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
10 | Partial Storage | 500 | 500 | 0 | 500 | 0 | 500 | 0 |  |  | 445.8333 | 54.1667 | 519.7917 | -19.7917
11 | Partial Storage | 800 | 800 | 0 | 800 | 0 | 800 | 0 |  |  | 445.8333 | 354.1667 | 519.7917 | 280.2083
12 | Partial Storage | 1000 | 960.373 | 39.627 | 1000 | 0 | -1019.2938 | 2019.2938 | x | -1019.2938 | 445.8333 | 554.1667 | 519.7917 | 480.2083
13 | Partial Storage | 1000 | 960.373 | 39.627 | 1000 | 0 | -1019.2938 | 2019.2938 | x | -1019.2938 | 445.8333 | 554.1667 | 519.7917 | 480.2083
14 | Partial Storage | 1000 | 960.373 | 39.627 | 1000 | 0 | -1019.2938 | 2019.2938 | x | -1019.2938 | 445.8333 | 554.1667 | 519.7917 | 480.2083
15 | Full Storage | 1000 | 0 | 1000 | 0 | 1000 | 0 | 1000 |  |  | 445.8333 | 1000 | 519.7917 | 1000
16 | Full Storage | 1000 | 0 | 1000 | 0 | 1000 | 0 | 1000 |  |  | 445.8333 | 1000 | 519.7917 | 1000
17 | Full Storage | 900 | 0 | 900 | 0 | 900 | 0 | 900 |  |  | 445.8333 | 900 | 519.7917 | 900
18 | Partial Storage | 800 | 800 | 0 | 800 | 0 | 800 | 0 |  |  | 445.8333 | 354.1667 | 519.7917 | 280.2083
19 | Partial Storage | 600 | 600 | 0 | 600 | 0 | 600 | 0 |  |  | 445.8333 | 154.1667 | 519.7917 | 80.2083
20 | Partial Storage | 600 | 600 | 0 | 600 | 0 | 600 | 0 |  |  | 445.8333 | 154.1667 | 519.7917 | 80.2083
21 | Partial Storage | 600 | 600 | 0 | 600 | 0 | 600 | 0 |  |  | 445.8333 | 154.1667 | 519.7917 | 80.2083
22 | Icemaking | 0 | 624.2424 | 0 | 995.3202 | 0 | 995.3202 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
23 | Icemaking | 0 | 624.2424 | 0 | 995.3202 | 0 | 995.3202 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
24 | Icemaking | 0 | 624.2424 | 0 | 995.3202 | 0 | 995.3202 | 0 |  |  | 445.8333 | 0 | 445.8333 | 0
Sum |  | 10700 | 13299.3007 | 3018.8811 | 16757.8814 | 2900 | 10700 | 8957.8814 |  |  | 10700 | 5787.5 | 11587.5 | 5121.875
Max |  | 1000 | 960.373 | 1000 | 1000 | 1000 | 995.3202 | 2019.2938 | 2019.2938 | -1019.2938 | 445.8333 | 1000 | 519.7917 | 1000
[9 empty] | 3 |  | 24
Icemaking hrs: | 9
Partial Storage hrs: | 9
Full Storage hrs: | 3
Diversity factor: | 71.33%
Min Chiller Size: | 960.373 | 464.6465 | 495.7265
2nd Partial Storage hrs: | 3 |  |  | 2900
2nd Chiller size: | 1531.2618 |  |  | 4461.5385
Storage ton-hrs: | 8957.8814 |  |  | 495.7265
Tanks: | 62
Charge t-h: | 8957.8814
Discharge2 t-h: | 2900
Max Original Output: | 1000
Hrs at max: | 3
Tons that can be shaven: | 2019.2938
3rd run chiller opt: | -1019.2938 | <---got to get the baseline
Hrs at or above chiller opt: | 24
available t-h: | 35163.0508
avg. >= max: | 445.8333
false t-h: | 1775

## v4
Icemaking
Partial Storage
Hour Ending | Chiller Plant Mode | Baseload | Variable load | Building Load (tons) | Full Storage Build/(Dispatch) | Full "chiller" available | Partial needs | Partial Chiller | P Chiller Ice Build/(Dispatch) | Initial Chiller Output | Initial Aggregated Loads | Full Storage
1 | Icemaking | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 362.7497 | 200 | 0 | Chiller Only
2 | Icemaking | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 362.7497 | 200 | 0
3 | Icemaking | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 362.7497 | 200 | 0
4 | Icemaking | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 362.7497 | 200 | 0
5 | Icemaking | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 362.7497 | 200 | 0
6 | Icemaking | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 362.7497 | 200 | 0
7 | Partial Storage | 200 | 200 | 400 | 0 | 0 | 200 | 200 | 0 | 400 | 400
8 | Partial Storage | 200 | 300 | 500 | 0 | 0 | 300 | 300 | 0 | 500 | 500
9 | Partial Storage | 200 | 400 | 600 | 0 | 0 | 400 | 400 | 0 | 600 | 600
10 | Partial Storage | 200 | 500 | 700 | 0 | 0 | 500 | 500 | 0 | 700 | 700
11 | Partial Storage | 200 | 800 | 1000 | 0 | 0 | 800 | 558.0765 | -241.9235 | 758.0765 | 1000
12 | Partial Storage | 200 | 1000 | 1200 | 0 | 0 | 1000 | 558.0765 | -441.9235 | 758.0765 | 1200
13 | Partial Storage | 200 | 1000 | 1200 | 0 | 0 | 1000 | 558.0765 | -441.9235 | 758.0765 | 1200
14 | Partial Storage | 200 | 1000 | 1200 | 0 | 0 | 1000 | 558.0765 | -441.9235 | 758.0765 | 1200
15 | Partial Storage | 200 | 1000 | 1200 | 0 | 0 | 1000 | 558.0765 | -441.9235 | 758.0765 | 1200
16 | Partial Storage | 200 | 1000 | 1200 | 0 | 0 | 1000 | 558.0765 | -441.9235 | 758.0765 | 1200
17 | Partial Storage | 200 | 900 | 1100 | 0 | 0 | 900 | 558.0765 | -341.9235 | 758.0765 | 1100
18 | Partial Storage | 200 | 800 | 1000 | 0 | 0 | 800 | 558.0765 | -241.9235 | 758.0765 | 1000
19 | Partial Storage | 200 | 600 | 800 | 0 | 0 | 600 | 558.0765 | -41.9235 | 758.0765 | 800
20 | Partial Storage | 200 | 600 | 800 | 0 | 0 | 600 | 558.0765 | -41.9235 | 758.0765 | 800
21 | Partial Storage | 200 | 600 | 800 | 0 | 0 | 600 | 558.0765 | -41.9235 | 758.0765 | 800
22 | Icemaking | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 362.7497 | 200 | 0
23 | Icemaking | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 362.7497 | 200 | 0
24 | Icemaking | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 362.7497 | 200 | 0
Sum |  | 4800 | 10700 | 15500 | 0 |  | 10700 |  | 103.5884
Max |  |  | 1000 |  | 0 |  | 1000 |  | 0
Full chiller "contr." | 0
Partial t-h | 10700
Icemaking hrs: | 9
Partial Storage hrs: | 15
Diversity of Partial hrs: | 71.33%
Effective Partial hrs: | 6.42
Partial chiller "contr." | 558.0765
Storage ton-hrs: | 3264.7473
Tanks: | 23

## v4 (2)
Icemaking
Partial Storage
Hour Ending | Chiller Plant Mode | Baseload | Variable load | Building Load (tons) | Full Storage Build/(Dispatch) | Full "chiller" available | Partial needs | Partial Chiller | P Chiller Ice Build/(Dispatch) | Initial Chiller Output | Initial Aggregated Loads | Final Aggregated Chiller | HE | Baseload Chiller | Dual-Duty Chiller | Ice Charge | Ice Discharge | Full Storage
1 | Icemaking | 200 | 0 | 200 | 100 | 0 | 0 | 0 | 307.0116 | 200 | 0 | 200 | 1 | 200 | 0 | 407.0116 | 0 | Chiller Only
2 | Icemaking | 200 | 0 | 200 | 100 | 0 | 0 | 0 | 307.0116 | 200 | 0 | 200 | 2 | 200 | 0 | 407.0116 | 0
3 | Icemaking | 200 | 0 | 200 | 100 | 0 | 0 | 0 | 307.0116 | 200 | 0 | 200 | 3 | 200 | 0 | 407.0116 | 0
4 | Icemaking | 200 | 0 | 200 | 100 | 0 | 0 | 0 | 307.0116 | 200 | 0 | 200 | 4 | 200 | 0 | 407.0116 | 0
5 | Icemaking | 200 | 0 | 200 | 100 | 0 | 0 | 0 | 307.0116 | 200 | 0 | 200 | 5 | 200 | 0 | 407.0116 | 0
6 | Icemaking | 200 | 0 | 200 | 100 | 0 | 0 | 0 | 307.0116 | 200 | 0 | 200 | 6 | 200 | 0 | 407.0116 | 0
7 | Full Storage | 200 | 200 | 400 | -400 | 153.8462 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 400
8 | Full Storage | 200 | 300 | 500 | -500 | 153.8462 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 500
9 | Partial Storage | 200 | 400 | 600 | 0 | 153.8462 | 246.1538 | 246.1538 | 0 | 600 | 600 | 600 | 9 | 200 | 400 | 0 | 0
10 | Partial Storage | 200 | 500 | 700 | 0 | 153.8462 | 346.1538 | 346.1538 | 0 | 700 | 700 | 700 | 10 | 200 | 500 | 0 | 0
11 | Partial Storage | 200 | 800 | 1000 | 0 | 153.8462 | 646.1538 | 472.3255 | -173.8284 | 826.1716 | 1000 | 792.112 | 11 | 200 | 592.112 | 0 | 173.8284
12 | Partial Storage | 200 | 1000 | 1200 | 0 | 153.8462 | 846.1538 | 472.3255 | -373.8284 | 826.1716 | 1200 | 792.112 | 12 | 200 | 592.112 | 0 | 373.8284
13 | Partial Storage | 200 | 1000 | 1200 | 0 | 153.8462 | 846.1538 | 472.3255 | -373.8284 | 826.1716 | 1200 | 792.112 | 13 | 200 | 592.112 | 0 | 373.8284
14 | Partial Storage | 200 | 1000 | 1200 | 0 | 153.8462 | 846.1538 | 472.3255 | -373.8284 | 826.1716 | 1200 | 792.112 | 14 | 200 | 592.112 | 0 | 373.8284
15 | Partial Storage | 200 | 1000 | 1200 | 0 | 153.8462 | 846.1538 | 472.3255 | -373.8284 | 826.1716 | 1200 | 792.112 | 15 | 200 | 592.112 | 0 | 373.8284
16 | Partial Storage | 200 | 1000 | 1200 | 0 | 153.8462 | 846.1538 | 472.3255 | -373.8284 | 826.1716 | 1200 | 792.112 | 16 | 200 | 592.112 | 0 | 373.8284
17 | Partial Storage | 200 | 900 | 1100 | 0 | 153.8462 | 746.1538 | 472.3255 | -273.8284 | 826.1716 | 1100 | 792.112 | 17 | 200 | 592.112 | 0 | 273.8284
18 | Partial Storage | 200 | 800 | 1000 | 0 | 153.8462 | 646.1538 | 472.3255 | -173.8284 | 826.1716 | 1000 | 792.112 | 18 | 200 | 592.112 | 0 | 173.8284
19 | Partial Storage | 200 | 600 | 800 | 0 | 153.8462 | 446.1538 | 446.1538 | 0 | 800 | 800 | 800 | 19 | 200 | 600 | 0 | 0
20 | Partial Storage | 200 | 600 | 800 | 0 | 153.8462 | 446.1538 | 446.1538 | 0 | 800 | 800 | 800 | 20 | 200 | 600 | 0 | 0
21 | Partial Storage | 200 | 600 | 800 | 0 | 153.8462 | 446.1538 | 446.1538 | 0 | 800 | 800 | 800 | 21 | 200 | 600 | 0 | 0
22 | Icemaking | 200 | 0 | 200 | 100 | 0 | 0 | 0 | 307.0116 | 200 | 0 | 200 | 22 | 200 | 0 | 407.0116 | 0
23 | Icemaking | 200 | 0 | 200 | 100 | 0 | 0 | 0 | 307.0116 | 200 | 0 | 200 | 23 | 200 | 0 | 407.0116 | 0
24 | Icemaking | 200 | 0 | 200 | 100 | 0 | 0 | 0 | 307.0116 | 200 | 0 | 200 | 24 | 200 | 0 | 407.0116 | 0
Sum |  | 4800 | 10700 | 15500 | 0 |  | 8200 |  | 272.4774
Max |  |  | 1000 |  | 100 |  | 846.1538 |  | 0 | 826.1716
Full chiller "contr." | 153.8462
Partial t-h | 8200
Icemaking hrs: | 9
Partial Storage hrs: | 13
Diversity of Partial hrs: | 74.55%
Effective Partial hrs: | 6.7091
Partial chiller "contr." | 472.3255
Storage ton-hrs: | 2763.1042
Plant Configuration
Baseload Chiller: | 200
Dual-Duty Chiller: | 627
IceBanks: | 20